SECTION 104413 - FIRE PROTECTION CABINETS

First Edition: 06-01-2021

(Consultant shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”)

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Fire-protection cabinets for the following:

            - Portable fire extinguisher.

            - Fire-hose valve.

        - Related Requirements:

          - Section 104416 "Fire Extinguishers" for portable, hand-carried fire extinguishers accommodated by fire-protection cabinets.

          - Section 211313 "Fire Protection Sprinkler and Standpipe Systems" for fire-hose connections.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Show door hardware, cabinet type, trim style, and panel style. Include roughing-in dimensions and details showing recessed-, semirecessed-, or surface-mounting method and relationships of box and trim to surrounding construction.

Retain subparagraph below for cabinet-mounted hose valves.

          - Show location of knockouts for hose valves.

        - Shop Drawings: For fire-protection cabinets.

          - Include plans, elevations, sections, details, and attachments to other work.

        - Product Schedule: For fire-protection cabinets. Indicate whether recessed, semirecessed, or surface mounted. Coordinate final fire-protection cabinet schedule with fire-extinguisher schedule to ensure proper fit and function. [Use same designations indicated on Drawings.]

      - COORDINATION

        - Coordinate size of fire-protection cabinets to ensure that type and capacity of [fire extinguishers] [hose valves] indicated are accommodated.

        - Coordinate sizes and locations of fire-protection cabinets with wall depths.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

Include when cabinets are in fire-rated partitions.

        - Fire-Rated Fire-Protection Cabinets: Listed and labeled to comply with requirements in ASTM E814 for fire-resistance rating of walls where they are installed.

      - FIRE-PROTECTION CABINET <Insert drawing designation>

        - Cabinet Type: Suitable for fire [extinguisher] [ or hose valve].

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Activar Construction Products Group, Inc. - JL Industries.

            - Guardian Fire Equipment, Inc.

            - Larsens Manufacturing Company.

            - Nystrom.

A/E to coordinate cabinet construction with requirements of wall construction.  Provide designations on the drawings if there are multiple types of cabinets.

        - Cabinet Construction: [Nonrated] [One-hour fire rated] [Two-hour fire rated].

Retain "Fire-Rated Cabinets" Subparagraph below for fire-rated cabinets.

          - Fire-Rated Cabinets: Construct fire-rated cabinets with double walls fabricated from 0.043-inch-thick cold-rolled steel sheet lined with minimum 5/8-inch-thick fire-barrier material. Provide factory-drilled mounting holes.

Steel is typical material for fire-protection cabinets and is required for fire-rated types.  For other cabinets pick painted or stainless steel based on existing building precedent if available.

        - Cabinet Material: [Cold-rolled steel sheet] [Stainless steel sheet].

        - Recessed Cabinet:

          - Exposed Flat Trim: One-piece combination trim and perimeter door frame overlapping surrounding wall surface, with exposed trim face and wall return at outer edge (backbend).

        - Semirecessed Cabinet: One-piece combination trim and perimeter door frame overlapping surrounding wall surface, with exposed trim face and wall return at outer edge (backbend).

          - Rolled-Edge Trim:  2-1/2-inch backbend depth.

        - Cabinet Trim Material:  [Steel Sheet ][Stainless steel sheet].

        - Door Material:  [Steel sheet][Stainless steel sheet].

        - Door Style: Vertical duo panel with frame.

        - Door Glazing:  [Clear float glass][Acrylic Sheet].

        - Door Hardware: Manufacturer's standard door-operating hardware of proper type for cabinet type, trim style, and door material and style indicated.

          - Provide projecting door pull and friction latch.  LOCKS ARE NOT ALLOWED.

          - Provide manufacturer's standard continuous hinge, permitting door to open 180 degrees.

        - Accessories:

          - Identification: Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location.

            - Identify fire extinguisher in fire-protection cabinet with the words "FIRE EXTINGUISHER."

              - Location: Applied to cabinet door.

              - Application Process:  Silk-screened.

              - Lettering Color:  Red- on metal face (not glass face).

              - Orientation:  Vertical.

        - Materials:

Edit below for selected materials.

          - Cold-Rolled Steel: ASTM A1008/A1008M, Commercial Steel (CS), Type B.

            - Finish:  Baked enamel, TGIC polyester powder coat, HAA polyester powder coat, epoxy powder coat, or polyester/epoxy hybrid powder coat, complying with AAMA 2603.

            - Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

            - Color: [As selected by Architect from manufacturer's full range] <Insert color>.

          - Stainless Steel: ASTM A240/A240M or ASTM A666, Type 304.

            - Finish:  ASTM A480/A480M No. 4 directional satin finish,.

          - Clear Float Glass: ASTM C1036, Type I, Class 1, Quality q3, 3 mm thick.

          - Transparent Acrylic Sheet: ASTM D4802, Category A-1 (cell-cast sheet), 3 mm thick, with Finish 1 (smooth or polished).

      - FABRICATION

        - Fire-Protection Cabinets: Provide manufacturer's standard box (tub) with trim, frame, door, and hardware to suit cabinet type, trim style, and door style indicated.

          - Weld joints and grind smooth.

          - Provide factory-drilled mounting holes.

        - Cabinet Doors: Fabricate doors according to manufacturer's standards, from materials indicated and coordinated with cabinet types and trim styles.

          - Fabricate door frames of one-piece construction with edges flanged

        - Cabinet Trim: Fabricate cabinet trim in one piece with corners mitered, welded, and ground smooth.

      - GENERAL FINISH REQUIREMENTS

        - Comply with NAAMM's AMP 500, "Metal Finishes Manual for Architectural and Metal Products," for recommendations for applying and designating finishes.

        - Protect mechanical finishes on exposed surfaces of fire-protection cabinets from damage by applying a strippable, temporary protective covering before shipping.

        - Finish fire-protection cabinets after assembly.

        - Appearance of Finished Work: Noticeable variations in same piece are unacceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for cabinets to verify actual locations of piping connections before cabinet installation.

        - Examine walls and partitions for suitable framing depth and blocking where recessed and semirecessed cabinets will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

Retain this article if Project includes recessed or semirecessed cabinets.

        - Prepare recesses for [recessed] [and] [semirecessed] fire-protection cabinets as required by type and size of cabinet and trim style.

      - INSTALLATION

        - General: Install fire-protection cabinets in locations and at mounting heights indicated or, if not indicated, at height indicated below:

          - Fire-Protection Cabinets: 42 inches above finished floor to top of fire extinguisher.

        - Fire-Protection Cabinets: Fasten cabinets to structure, square and plumb.

          - Unless otherwise indicated, provide recessed fire-protection cabinets. If wall thickness is inadequate for recessed cabinets, provide semirecessed fire-protection cabinets.

Retain subparagraph below if Project includes fire-rated hose-valve cabinets.

          - Fire-Rated Hose-Valve Cabinets:

            - Install cabinet with not more than 1/16-inch tolerance between pipe OD and knockout OD. Center pipe within knockout.

            - Seal through penetrations with firestopping sealant as specified in Division 07 Section "Penetration Firestopping."

        - Identification:

          - Apply decals in vertical position on metal surface for fire-extinguisher cabinets.

      - ADJUSTING AND CLEANING

        - Remove temporary protective coverings and strippable films, if any, as fire-protection cabinets are installed unless otherwise indicated in manufacturer's written installation instructions.

        - Adjust fire-protection cabinet doors to operate easily without binding. Verify that integral locking devices operate properly.

        - On completion of fire-protection cabinet installation, clean interior and exterior surfaces as recommended by manufacturer.

        - Touch up marred finishes or replace fire-protection cabinets that cannot be restored to factory-finished appearance. Use only materials and procedures recommended or furnished by fire-protection cabinet and mounting bracket manufacturers.

        - Replace fire-protection cabinets that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

END OF SECTION 104413