SECTION 261116 - SECONDARY UNIT SUBSTATIONS

Latest Update 5-6-2017 See underlined text for Edits.

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn of all “Underlines”.)

Last Update: 6.9.11. Reformatted and See Underlined Text.

GENERAL

      - RELATED DOCOMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this section and all other sections of Division 26.

SUMMARY

This Section includes indoor and outdoor secondary unit substations, each consisting of the following:

Primary incoming section.

Transformer.

Secondary distribution section.

DEFINITIONS

NETA ATS:  Acceptance Testing Specification.

SUBMITTALS

Product Data:  Include rated capacities, furnished specialties, and accessories.

Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Wiring Diagrams:  Power, signal, and control wiring.

Dimensioned plans and elevations showing major components and features.

One-line diagram.

List of materials.

Nameplate legends.

Size and number of bus bars and current rating for each bus, including mains and branches of phase, neutral, and ground buses.

Short-time and short-circuit current ratings of secondary unit substations and components.

Ratings of individual protective devices.

Time-Current Characteristic Curves:  For overcurrent protective devices.

Primary Fuses:  Submit recommendations and size calculations.

Coordination Drawings: Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Dimensioned concrete base, outline of secondary unit substation, conduit entries, and ground rod locations.

Location of structural supports for structure-supported raceways and busways.

Location of lighting fixtures, sprinkler piping and heads, ducts, and diffusers.

Product Certificates:  For secondary unit substations, signed by product manufacturer.

Qualification Data:  For independent testing agency.

Material Test Reports:  For secondary unit substations.

Factory test reports.

Field quality-control test reports.

Operation and Maintenance Data: For secondary unit substations and accessories to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

Independent Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

Testing Agency's Field Supervisor: Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

Source Limitations:  Obtain secondary unit substation through one source from a single manufacturer.

Product Options: Drawings indicate size, profiles, and dimensional requirements of secondary unit substations and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

Electrical Components, Devices and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Comply with IEEE C2.

Comply with IEEE C37.121.

Comply with NFPA 70.

DELIVERY, STORAGE, AND HANDLING

Delete first paragraph below if no known obstacles to movement of normal shipping, lengths of secondary unit substations, and substation sections.  Coordinate with Drawings.

Deliver in shipping splits in sizes that can be moved past obstructions in delivery path.

Coordinate delivery of secondary unit substations to allow movement into designated space.

Store secondary unit substation components protected from weather and so condensation will not form on or in units. Provide temporary heating according to manufacturer's written instructions.

Handle secondary unit substation components according to manufacturer's written instructions.  Use factory-installed lifting provisions.

PROJECT CONDITIONS

Field Measurements:  Indicate measurements on Shop Drawings.

Delete first paragraph and subparagraphs below if no interruption of existing electric service is required.

Interruption of Existing electric Service:  Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

Notify UM no fewer than 10 days in advance of proposed interruption of electric service.

Do not proceed with interruption of electric service without UM’s written permission.

Service Conditions:  IEEE C37.121, usual service conditions, except for the following:

Select and modify conditions below and specify features required to provide satisfactory service.

Exposure to significant solar radiation.

Altitudes above 3300 feet.

Exposure to fumes, vapors, or dust.

Exposure to explosive environments.

Exposure to hot and humid climate or to excessive moisture, including steam, salt spray, and dripping water.

Exposure to seismic shock or to abnormal vibration, shock, or tilting.

Exposure to excessively high or low temperatures.

Unusual transportation or storage conditions.

Unusual grounding resistance conditions.

Unusual space limitations.

COORDINATION

Coordinate layout and installation of secondary unit substations with other construction that penetrates floors and ceilings, or is supported by them, including light fixtures, HVAC equipment, and fire-suppression-system components.

Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

EXTRA MATERIALS

Furnish extra materials described below, before installation begins, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Spare fuses: 10% of total for project; each type and rating of fuse and fusible device used, except for medium-voltage fuses.  Include spares for the following:

Primary disconnect fuses.

Potential transformer fuses.

Control power fuses.

Fuses and fusible devices for fused circuit breakers.

Fuses for secondary fusible devices.

Spare Indicating Lights:  Six of each type installed.

Touchup Paint:  [Three] <Insert number> half-pint containers of paint matching enclosure's exterior finish.

Primary Switch Contact Lubricant:  [One] <Insert number> container(s).

[One] <Insert number> set(s) of spare mounting gaskets for bushings, handholes, and the gasket between relief cover and flange of pressure relief device

WARRANTY/GUARANTEE

See Division 26 Specification Section “Basic Electrical Requirements’ for warranty and guarantee requirements.

PRODUCTS

MANUFACTURERS

Manufacturers: Subject to compliance with requirements, provide products by one (1) of the following:

ABB Control, Inc.

Cooper Industries, Inc.; Cooper Power Systems Division.

Cutler-Hammer.

Square D; Schneider Electric.

MANUFACTURED UNITS

Indoor Unit Arrangement:  Single assembly.

Retain paragraph above or first paragraph below for indoor units.

Indoor Unit Arrangement: Separate secondary distribution equipment connected with busway.

Outdoor Unit Arrangement: [Single assembly] [Separate secondary distribution equipment connected with busway] <Insert arrangement>.

Weatherproof, listed for installation outdoors, complying with IEEE C37.20.1.

Aisleless Construction: Full-height doors in front of basic weatherproof equipment.

Enclosure Finish: Factory-applied finish in manufacturer's standard color, including under surfaces treated with corrosion-resistant undercoating.

Select paragraph above for outdoor units or below for indoor units.

Enclosure Finish: Factory-applied finish in manufacturer's standard gray over a rust-inhibiting primer on treated metal surface.

INCOMING SECTION

Primary Incoming Section:  Enclosed, air-interrupter, [dual primary] [primary] switch.

Three pole, single throw, dead front, metal enclosed, with manual stored energy operator, frame complying with IEEE C37.20.3.

Key interlocking system to prevent fuse access door from being opened unless switch is open

Allow non-interlock operation of dual primary switches.

Phase Barriers:  Located between blades and fuses of each phase, designed for easy removal, allows visual inspection of switch components when barrier is in place.

IR Port:  3 inches.

Window:  Permits viewing switch-blade positions when door is closed.

Accessory Set:  Tools and miscellaneous items required for interrupter switchgear test, inspection, maintenance, and operation. Include fuse-handling tool as recommended by switchgear manufacturer.

Continuous-current and short-circuit ratings listed below are for commonly available switches; adjust if required to suit Project conditions.

Continuous-Current Rating:  600 A.

Short-Circuit Rating:

Short-time momentary asymmetrical fault rating of 40 kA.

2-second symmetrical rating of 25-kA RMS.

Fault close asymmetrical rating of 40 kA.

Fuses: Sizes recommended by secondary unit substation manufacturer, considering fan cooling, temperature-rise specification, and cycle loading.  Comply with the following:

Current-limiting type, rated for not less than 50-kA RMS symmetrical current-interrupting capacity.

Indicator integral with each fuse to show when it has blown.

Spares:  Include three fuses in use and three spare fuses in storage clips in each switch.

Revise paragraph below to specify station or intermediate-class arresters if Project conditions require.

Surge Arresters: Comply with IEEE C62.11, Distribution class; metal-oxide-varistor type, with ratings as indicated, connected in each phase of incoming circuit and ahead of any disconnecting device.  Comply with IEEE.

LIQUID-FILLED TRANSFORMER SECTION

Retain this Article for liquid-filled transformers or delete and retain "Dry-Type Transformer Section" Article.

Description: IEEE C57.12.00 and UL 1062, liquid-filled, 2-winding, secondary unit substation transformer.

Insulating Liquid: Mineral oil complying with ASTM D 3487, Type II, and tested according to ASTM D 117.

Delete paragraph above if less-flammable insulating liquid is required. Transformer primary voltage must be 35 kV or less for less-flammable liquids.  Insulating Liquid:  less flammable, silicone-based dielectric and UL listed as complying with NFPA 70 requirements for fire point of not less than 300 deg C when tested according to ASTM D 92.  Liquid shall have low toxicity and be nonhazardous.

Insulation Temperature Rise:  650C/550C, based on an average ambient temperature of 300C over 24 hours with a maximum ambient temperature of 400C.  Insulation system shall be rated to continuously allow an additional 12-percent kVA output, at 650C temperature rise, without decreasing rated transformer life.

Basic Impulse Level:  [60] [95] kV.  Comply with UL 1062.

Full-Capacity Voltage Taps: 4 nominal 2.5% taps, 2 above and 2 below rated primary voltage; with externally operable tap changer for de-energized use and with position indicator and padlock hasp.

Cooling System: Class OA/FA, liquid cooled, and with forced-air rating.  Cooling systems shall include auxiliary cooling equipment, automatic controls, and status indicating lights.

Sound level may not exceed 58 dB, without fans.

Impedance:  5.75%.

Accessories: Grounding pads, lifting lugs, and provisions for jacking under base.  Transformers shall have a steel base and frame allowing use of pipe rollers in any direction, and an insulated, low-voltage, neutral bushing with removable ground strap.  Include the following additional accessories:

Liquid-level gage.

Pressure-vacuum gage.

Liquid temperature indicator.

Drain and filter valves.

Pressure relief device.

Remote monitoring capability and equipment

DRY-TYPE TRANSFORMER SECTION

Description:  IEEE C57.12.01, [IEEE C57.12.50] [IEEE C57.12.51] [IEEE C57.12.52], NEMA ST 20, and dry-type, 2-winding, secondary unit substation transformer.

Enclosure:  [Indoor, ventilated] [cast coil/encapsulated coil, with primary and secondary windings individually cast in epoxy] <Insert enclosure type>; with insulation system rated at 1850C with an 800C average winding temperature rise above a maximum ambient temperature of 400 C.

Cooling System:  Class [AA/FA, air cooled with forced-air rating] complying with IEEE C57.12.01.

Automatic forced-air cooling system controls, including thermal sensors, fans, control wiring, temperature controller with test switch, power panel with current-limiting fuses, indicating lights, alarm, and alarm silencing relay.

Insulation Materials:  IEEE C57.12.01, rated 2200C.

Insulation Temperature Rise:  800C, maximum rise above 400C.

Basic Impulse Level:  95 kV.

Full-Capacity Voltage Taps: 4 nominal 2.5% taps, 2 above and two (2) below rated primary voltage.

Sound level may not exceed 64dBA level, without fans operating.

Impedance:  5.75 percent.

If retaining paragraph below, coordinate with Drawings and provide external power and signal connections.

J.	High-Temperature Alarm:  Sensor at transformer with local audible and visual alarm and contacts for remote alarm.  Provide Square D Model 98 transformer temperature monitor for remote recording of transformer winding temperatures.

SECONDARY DISTRIBUTION SECTION

Retain one of first three paragraphs below.

Secondary Distribution:  Low-voltage switchgear as specified in Division 26 Section "Low-Voltage Switchgear."

Secondary Distribution: Low-voltage switchboard as specified in Division 26 Section "Switchboards."

Distribution Panelboard: Panelboards as specified in Division 26 Section "Panelboards."

IDENTIFICATION DEVICES

Compartment Nameplates: Engraved, laminated-plastic or metal nameplate for each compartment, mounted with corrosion-resistant screws.  Nameplates and label products are specified in Division 26 Section "Identification for Electrical Systems."

SOURCE QUALITY CONTROL

Factory Tests: Perform design and routine tests according to standards specified for components. Conduct transformer tests according to IEEE C57.12.90. Conduct switchgear and switchboard tests according to ANSI C37.51.

Factory Tests: Perform the following factory-certified tests on each secondary unit substation:

Resistance measurements of all windings on the rated voltage connection and on tap extreme connections.

Ratios on the rated voltage connection and on tap extreme connections.

Polarity and phase relation on the rated voltage connection.

No-load loss at rated voltage on the rated voltage connection.

Exciting current at rated voltage on the rated voltage connection.

Impedance and load loss at rated current on the rated voltage connection and on tap extreme connections.

Applied potential.

Induced potential.

Temperature Test:  If a transformer is supplied with auxiliary cooling equipment to provide more than one rating, test at lowest kilovolt-ampere Class OA or Class AA rating and highest kilovolt-ampere Class FA rating.

Temperature test is not required if a record of a temperature test on an essentially duplicate unit is available.

Owner will witness all required factory tests. Contractor to provide accommodations if more than 50 mi from site.  Notify Architect at least 14 days before date of tests and indicate their approximate duration.

EXECUTION

EXAMINATION

Examine areas and space conditions for compliance with requirements for secondary unit substations and other conditions affecting performance of work.

Examine roughing-in of conduits and grounding systems to verify the following:

Wiring entries comply with layout requirements.

Entries are within conduit-entry tolerances specified by manufacturer and no feeders will have to cross section barriers to reach load or line lugs.

Examine walls, floors, roofs, and concrete bases for suitable conditions for secondary unit substation installation.

Verify that ground connections are in place and that requirements in Division 26 Section "Grounding and Bonding for Electrical Systems" have been met.  Maximum ground resistance shall be 5 ohms at secondary unit substation location.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install secondary unit substations on concrete bases.

Construct concrete bases of dimensions indicated, but not less than 4 inches larger in both directions than supported unit and 4 inches high.

Use [3,000-psi] <Insert other>, twenty eight (28) day compressive-strength concrete and reinforcement as specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

Maintain minimum clearances and workspace at equipment according to manufacturer's written instructions and NFPA 70.

IDENTIFICATION

Identify field-installed wiring and components and provide warning signs as specified in Division 26 Section "Identification for Electrical Systems."

Operating Instructions: Frame printed operating instructions for secondary unit substations, including key interlocking, control sequences, elementary single-line diagram, and emergency procedures.  Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic. Mount on front of secondary unit substation.

CONNECTIONS

Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

CLEANING

After completing equipment installation and before energizing, inspect unit components.  Remove paint splatters and other spots, dirt, and debris.  Repair damaged finish to match original finish.  Vacuum interiors of secondary unit substation sections.

FIELD QUALITY CONTROL

Manufacturer's Field Service: Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including connections.  Report results in writing.

Testing: Engage a qualified independent testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

Perform each visual and mechanical inspection and electrical test according to NETA ATS.  Certify compliance with test parameters.

After installing secondary unit substation but before primary is energized, verify that grounding system at the substation tested at the specified value or less.

After installing secondary unit substation and after electrical circuitry has been energized, test for compliance with requirements.

Set field-adjustable switches and circuit-breaker trip ranges as indicated and per short circuit analysis and recommendations of coordination.

Remove and replace malfunctioning units and retest as specified above.

FOLLOW-UP SERVICE

Voltage Monitoring and Adjusting: After Substantial Completion, if requested by Owner, but not more than six months after Final Acceptance, perform the following voltage monitoring:

During a period of normal load cycles as evaluated by Owner, perform seven days of three-phase voltage recording at the outgoing section of each secondary unit substation. Use voltmeters with calibration traceable to the National Institute of Science and Technology standards and with a chart speed of not less than 1 inch per hour.  Voltage unbalance greater than 1 percent between phases, or deviation of any phase voltage from the nominal value by more than plus or minus 5% during the test period, is unacceptable.

Corrective Action: If test results are unacceptable, perform the following corrective action, as appropriate:

Adjust transformer taps.

Rebalance loads.

Prepare written request for voltage adjustment by electric utility.

Retests: Repeat monitoring, after corrective action has been performed, until satisfactory results are obtained.

Report: Present field copy and prepare a written report covering monitoring performed and corrective action taken.

Infrared Scanning:  Perform as specified in Division 26 Section "Medium-Voltage Switchgear."

DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain systems. Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 261116