**SECTION 262413 - SWITCHBOARDS**

Latest Update 5-6-2917 See underlined text for Edits.

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”.)Last Update: 6.9.11. Reformatted and See Underlined Text.

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project.)

1. **GENERAL**
   * + 1. RELATED DOCUMENTS
          1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this section and all other sections of Division 26.
       2. SUMMARY
          1. Section Includes:

Service and distribution switchboards rated 600 V and less.

Transient voltage suppression devices.

Disconnecting and overcurrent protective devices.

Instrumentation.

Control power.

Accessory components and features.

Identification.

* + - 1. SUBMITTALS
         1. Product Data: For each type of switchboard, overcurrent protective device, transient voltage suppression device, ground-fault protector, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, accessories, and finishes.
         2. Shop Drawings: For each switchboard and related equipment.

Include dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment. Show tabulations of installed devices, equipment features, and ratings.

Detail enclosure types for types other than NEMA 250, Type 1.

Detail bus configuration, current, and voltage ratings.

Detail short-circuits current rating of switchboards and overcurrent protective devices.

Include descriptive documentation of optional barriers specified for electrical insulation and isolation.

Detail utility company's metering provisions with indication of approval by utility company.

Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

Include time-current coordination curves for each type and rating of overcurrent protective device included in switchboards. Include selectable ranges for each type of overcurrent protective device.

Include schematic and wiring diagrams for power, signal, and control wiring.

* + - * 1. Qualification Data: For qualified testing agency.
        2. Field Quality-Control Reports:

Test procedures used.

Test results that comply with requirements.

Results of failed tests and corrective action taken to achieve test results that comply with requirements.

* + - * 1. Operation and Maintenance Data: For switchboards and components to include in emergency, operation, and maintenance manuals. In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

Routine maintenance requirements for switchboards and all installed components.

Manufacturer's written instructions for testing, maintaining and adjusting overcurrent protective devices.

Time-current coordination curves for each type and rating of overcurrent protective device included in switchboards. Include selectable ranges for each type of overcurrent protective device.

* + - 1. QUALITY ASSURANCE
         1. Installer Qualifications: An employer of workers qualified as defined in NEMA PB 2.1 and trained in electrical safety as required by NFPA 70E.
         2. Testing Agency Qualifications: Member Company of NETA or an NRTL.

Testing Agency's Field Supervisor: Currently certified by NETA to supervise on-site testing.

* + - * 1. Source Limitations: Obtain switchboards, overcurrent protective devices, components, and accessories from single source from single manufacturer.
        2. Product Selection for Restricted Space: Drawings indicate maximum dimensions for switchboards including clearances between switchboards and adjacent surfaces and other items. Comply with indicated maximum dimensions.
        3. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.
        4. Comply with NEMA PB 2.
        5. Comply with NFPA 70.
        6. Comply with UL 891.
      1. DELIVERY, STORAGE, AND HANDLING
         1. Deliver switchboards in sections or lengths that can be moved past obstructions in delivery path.
         2. Remove loose packing and flammable materials from inside switchboards and [install temporary electric heating (250 W per section)] [connect factory-installed space heaters to temporary electrical service] to prevent condensation. <Engineer to Edit for Project Requirements>
         3. Handle and prepare switchboards for installation according to NEMA PB 2.1.
      2. PROJECT CONDITIONS
         1. Installation Pathway: Remove and replace access fencing, doors, lift-out panels, and structures to provide pathway for moving switchboards into place.
         2. Environmental Limitations:

Do not deliver or install switchboards until spaces are enclosed and weather-tight, wet work in spaces is complete and dry, work above switchboards is complete, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

Rate equipment for continuous operation under the following conditions unless otherwise indicated:

Ambient Temperature: Not exceeding 1040F (400C).

Altitude: Not exceeding 6600 feet (2000 m).

* + - * 1. Interruption of Existing Electric Service: Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

Notify UMB, in writing, no fewer than 10 days in advance of proposed interruption of electric service.

Indicate method of providing temporary electric service.

Do not proceed with interruption of electric service without UMB’s written permission.

Comply with NFPA 70E.

* + - 1. COORDINATION
         1. Coordinate layout and installation of switchboards and components with other construction that penetrates walls or is supported by them, including electrical and other types of equipment, raceways, piping, encumbrances to workspace clearance requirements, and adjacent surfaces. Maintain required workspace clearances and required clearances for equipment access doors and panels.
         2. Coordinate sizes and locations of concrete bases with actual equipment provided. Cast anchor-bolt inserts into bases. Concrete, reinforcement, and formwork requirements are specified in Division 03.
      2. WARRANTY
         1. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Warranty Period: Five years from date of Substantial Completion.

* + - 1. EXTRA MATERIALS
         1. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Potential Transformer Fuses: Equal to 10% of quantity installed for each size and type, but no fewer than two (2) of each size and type.

Control-Power Fuses: Equal to 10 % of quantity installed for each size and type, but no fewer than two (2) of each size and type.

Fuses and Fusible Devices for Fused Circuit Breakers: Equal to 10 % of quantity installed for each size and type, but no fewer than three (3) of each size and type.

Fuses for Fused Switches: Equal to 10 % of quantity installed for each size and type, but no fewer than three (3) of each size and type.

Fuses for Fused Power-Circuit Devices: Equal to 10 % of quantity installed for each size and type, but no fewer than three (3) of each size and type.

Indicating Lights: Equal to 10 % of quantity installed for each size and type, but no less than one of each size and type.

Provide Fuse cabinet, to location coordinated with Owner.

* + - 1. WARRANTY/GUARANTEE
         1. See Division 26 Specification Section “Basic Electrical Requirements’ for warranty and guarantee requirements.

1. **PRODUCTS**
   * + 1. MANUFACTURED UNITS
2. Basis-of-Design Product: Subject to compliance with requirements, provide product by one (1) of the following:

Eaton Electrical Inc.; Cutler-Hammer Business Unit.

Siemens Energy & Automation, Inc.

Square D; a brand of Schneider Electric.

Specify particular side access is available.

* + - * 1. Front- and Side-Accessible Switchboards:

Main Devices: Fixed, individually mounted.

Branch Devices: Panel mounted.

Sections front and rear aligned.

* + - * 1. Nominal System Voltage: [480Y/277 V] [208Y/120 V]. <Engineer to Edit for Project Requirements>
        2. Main-Bus Continuous: [4000] [3000] [2500] [2000] [1600] [1200] A. <Engineer to Edit for Project Requirements>
        3. Indoor Enclosures: Steel, NEMA 250, Type 1.
        4. Enclosure Finish for Indoor Units: Factory-applied finish in manufacturer’s ANSI 49 gray finish over a rust-inhibiting primer on treated metal surface.
        5. Customer Metering Compartment: A separate customer metering compartment and section with front hinged door, for indicated metering, and current transformers for each meter. Current transformer secondary wiring shall be terminated on shorting-type terminal blocks. [Include potential transformers having primary and secondary fuses with disconnecting means and secondary wiring terminated on terminal blocks.] <Engineer to Edit for Project Requirements>
        6. Bus Transition and Incoming Pull Sections: Matched and aligned with basic switchboard.
        7. Hinged Front Panels: Allow access to circuit breaker, metering, accessory, and blank compartments.
        8. Pull Box on Top of Switchboard:

Adequate ventilation to maintain temperature in pull box within same limits as switchboard.

Set back from front to clear circuit-breaker removal mechanism.

Removable covers shall form top, front, and sides. Top covers at rear shall be easily removable for drilling and cutting.

Bottom shall be insulating, fire-resistive material with separate holes for cable drops into switchboard.

Cable supports shall be arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

* + - * 1. Buses and Connections: Three-phase, four-wire unless otherwise indicated.

Phase- and Neutral-Bus Material: Hard-drawn copper of 98 percent conductivity, with copper feeder circuit-breaker line connections.

Ground Bus: [1/4-by-2-inch] [1/4-by-1-inch] [Minimum-size required by UL 891] hard-drawn copper of 98 % conductivity, equipped with mechanical connectors for feeder and branch-circuit ground conductors. For busway feeders, extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run. <Engineer to Edit for Project Requirements>

Main Phase Buses and Equipment Ground Buses: Uniform capacity for entire length of switchboard's main and distribution sections. Provide for future extensions from both ends.

Neutral Buses: 100 % of the ampacity of phase buses unless otherwise indicated, equipped with mechanical connectors for outgoing circuit neutral cables. Brace bus extensions for busway feeder neutral bus.

* + - * 1. Future Devices: Equip compartments with mounting brackets, supports, bus connections, and appurtenances at full rating of circuit-breaker compartment.
      1. TRANSIENT VOLTAGE SUPPRESSION DEVICES
         1. Basis-of-Design Product: Subject to compliance with requirements, provide product by one (1)of the following:

Eaton Electrical Inc.; Cutler-Hammer Business Unit.

Siemens Energy & Automation, Inc.

Square D; a brand of Schneider Electric.

* + - * 1. Surge Protection Device Description: IEEE C62.41-compliant, exterior mounted units , wired-in, solid-state, parallel-connected, modular (with field-replaceable modules) type, with sine-wave tracking suppression and filtering modules, ANSI Rev 2 and UL 1449, second edition, short-circuit current rating matching or exceeding the switchboard short-circuit rating, and with the following features and accessories:

Fuses, rated at 200-kA interrupting capacity.

Fabrication using bolted compression lugs for internal wiring.

Redundant suppression circuits.

Redundant replaceable modules.

Arrangement with wire connections to phase buses, neutral bus, and ground bus.

LED indicator lights for power and protection status.

Audible alarm, with silencing switch, to indicate when protection has failed.

Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of system operation. Contacts shall reverse position on failure of any surge diversion module or on opening of any current-limiting device. Coordinate with building power monitoring and control system.

[Four] [Six]<Insert number>-digit, transient-event counter set to totalize transient surges.

* + - * 1. Peak Single-Impulse Surge Current Rating: 120 kA per mode/240 kA per phase.
        2. Withstand Capabilities: 12,000 IEEE C62.41, Category C3 (10 kA), 8-by-20-micro-second surges with less than 5% change in clamping voltage.
        3. Protection modes and UL 1449 SVR for grounded wye circuits with [480Y/277] [208Y/120] -V, three-phase, four-wire circuits shall be as follows:

Line to Neutral: [600 V for 480Y/277] [330 V for 208Y/120].

Line to Ground: [600 V for 480Y/277] [330 V for 208Y/120].

Neutral to Ground: [600 V for 480Y/277] [330 V for 208Y/120].

<Engineer to Edit for Project Requirements>

* + - * 1. Protection modes and UL 1449 SVR for 480-, or 600-V, three-phase, three-wire, delta circuits shall be as follows:

Line to Line: [2000 V for 480 V] [2500 V for 600 V].

Line to Ground: [1500 V for 480 V] [2500 V for 600 V].

<Engineer to Edit for Project Requirements>

* + - 1. DISCONNECTING AND OVERCURRENT PROTECTIVE DEVICES
         1. Molded-Case Circuit Breaker (MCCB): Comply with UL 489, with interrupting capacity to meet available fault currents.

Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Instantaneous trip.

Long- and short-time pickup levels.

Long- and short-time time adjustments.

Ground-fault pickup level, time delay, and I2t response.

Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

Integrally Fused Circuit Breakers: Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

Retain first subparagraph below for GFCI circuit breakers for personnel ground-fault protection as required by NFPA 70; retain second subparagraph for GFEP circuit breakers (e.g., for self-limiting heat-trace cables) as required by NFPA 70. GFCI and GFEP circuit breakers are only available fully rated up to interrupting ratings of 22 kA and are not suited to switchboard use. For switchboards subject to fault currents above 22 kA, series ratings must be used.

GFCI Circuit Breakers: Single- and two-pole configurations with Class A ground-fault protection (6-mA trip).

Ground-Fault Equipment Protection (GFEP) Circuit Breakers: Class B ground-fault protection (30-mA trip).

Molded-Case Circuit-Breaker (MCCB) Features and Accessories:

Standard frame sizes, trip ratings, and number of poles.

Lugs: Mechanical style, suitable for number, size, trip ratings, and conductor material.

Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator. <Engineer to Edit for Project Requirements>

Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

Communication Capability: [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system specified in Division 26 Section "Electrical Power Monitoring and Control." <Engineer to Edit for Project Requirements>

Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

Undervoltage Trip: Set to operate at 35% to 75 % of rated voltage without intentional time delay.

Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts. <Engineer to Edit for Project Requirements>

Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

* + - * 1. Insulated-Case Circuit Breaker (ICCB): 80 % rated, sealed, insulated-case power circuit breaker with interrupting capacity rating to meet available fault current.

Fixed circuit-breaker mounting.

Two-step, stored-energy closing.

Standard-function, microprocessor-based trip units with interchangeable rating plug, trip indicators, and the following field-adjustable settings:

Long- and short-time time adjustments.

Ground-fault pickup level, time delay, and I2t response.

Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

Remote trip indication and control.

Communication Capability: Integral communication module with functions and features compatible with power monitoring and control system specified in Division 26 Section "Electrical Power Monitoring and Control."

Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

Control Voltage: 120-V ac.

* + - * 1. Bolted-Pressure Contact Switch: Operating mechanism uses rotary-mechanical-bolting action to produce and maintain high clamping pressure on the switch blade after it engages the stationary contacts.

Manufacturers: Provide products by one (1) of the following:

Eaton Electrical Inc.; Cutler-Hammer Business Unit.

Siemens Energy & Automation, Inc.

Square D; a brand of Schneider Electric.

Main-Contact Interrupting Capability: Minimum of twelve (12) times the switch current rating.

Operating Mechanism: Manual handle operations to close switch; stores energy in mechanism for opening and closing.

Electrical Trip: Operation of lever or push-button trip switch, or trip signal from ground-fault relay or remote-control device, causes switch to open.

Auxiliary Switches: Factory installed, single pole, double throw, with leads connected to terminal block, and including one set more than quantity required for functional performance indicated.

Service-Rated Switches: Labeled for use as service equipment.

Ground-Fault Relay: Comply with UL 1053; self-powered type with mechanical ground-fault indicator, test function, tripping relay with internal memory, and three-phase current transformer/sensor.

Configuration: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator. <Engineer to Edit for Project Requirements>

Internal Memory: Integrates the cumulative value of intermittent arcing ground-fault currents and uses the effect to initiate tripping.

No-Trip Relay Test: Permits ground-fault simulation test without tripping switch.

Test Control: Simulates ground fault to test relay and switch (or relay only if "no-trip" mode is selected).

Open-Fuse Trip Device: Arranged to trip switch open if a phase fuse opens.

* + - 1. INSTRUMENTATION – Refer to Section 262713 “Electricity Metering” & 260913 “Electrical Power Monitoring & Control”
      2. CONTROL POWER
         1. Control Circuits: 120-V ac, supplied through secondary disconnecting devices from control-power transformer.
         2. Electrically Interlocked Main and Tie Circuit Breakers: Two control-power transformers in separate compartments, with interlocking relays, connected to the primary side of each control-power transformer at the line side of the associated main circuit breaker. 120-V secondary’s connected through automatic transfer relays to ensure a fail-safe automatic transfer scheme.
         3. Control-Power Fuses: Primary and secondary fuses for current-limiting and overload protection of transformer and fuses for protection of control circuits.
         4. Control Wiring: Factory installed, with bundling, lacing, and protection included. Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.
      3. ACCESSORY COMPONENTS AND FEATURES
         1. Portable Test Set: For testing functions of solid-state trip devices without removing from switchboard. Include relay and meter test plugs suitable for testing switchboard meters and switchboard class relays.

Retain paragraph below if fuse cabinet is not specified in Division 26 Section "Fuses."

* + - * 1. Spare-Fuse Cabinet: Suitably identified, wall-mounted, lockable, compartmented steel box or cabinet. Arrange for wall mounting.
      1. IDENTIFICATION
         1. Service Equipment Label: NRTL labeled for use as service equipment for switchboards with one or more service disconnecting and overcurrent protective devices.
         2. Permanent Engraved Phenolic Nameplates: Provide white with black lettering ID plates for each circuit.

1. **EXECUTION**
   * + 1. EXAMINATION
          1. Receive, inspect, handle, and store switchboards according to NEMA PB 2.1.
          2. Examine switchboards before installation. Reject switchboards that are moisture damaged or physically damaged.
          3. Examine elements and surfaces to receive switchboards for compliance with installation tolerances and other conditions affecting performance of the Work.
          4. Proceed with installation only after unsatisfactory conditions have been corrected.
       2. INSTALLATION
          1. Install switchboards and accessories according to NEMA PB 2.1.
          2. Equipment Mounting: Install switchboards on concrete base, four (4) inch (100-mm) nominal thickness. Comply with requirements for concrete base specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on eighteen (18) inch (450-mm) centers around the full perimeter of concrete base.

For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

Install anchor bolts to elevations required for proper attachment to switchboards.

* + - * 1. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.
        2. Operating Instructions: Frame and mount the printed basic operating instructions for switchboards, including control and key interlocking sequences and emergency procedures. Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic. Mount on front of switchboards.
        3. Install filler plates in unused spaces of panel-mounted sections.
        4. Install overcurrent protective devices, transient voltage suppression devices, and instrumentation.
        5. Set field-adjustable switches and circuit-breaker trip ranges as specified in Division 26 Section "Overcurrent Protective Device Coordination Study."Install spare-fuse cabinet.
        6. Comply with NECA 1.
      1. CONNECTIONS
         1. Comply with requirements for terminating feeder bus specified in Division 26 Section "Enclosed Bus Assemblies." Drawings indicate general arrangement of bus, fittings, and specialties.
         2. Comply with requirements for terminating cable trays specified in Division 26 Section "Cable Trays for Electrical Systems." Drawings indicate general arrangement of cable trays, fittings, and specialties.
      2. IDENTIFICATION
         1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."
         2. Switchboard Nameplates: Label each switchboard compartment with a nameplate complying with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."
         3. Device Nameplates: Label each disconnecting and overcurrent protective device and each meter and control device mounted in compartment doors with a nameplate complying with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."
      3. FIELD QUALITY CONTROL
         1. Testing Agency: Engage a qualified testing agency to perform tests and inspections.
         2. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

* + - * 1. Acceptance Testing Preparation:

Test insulation resistance for each switchboard bus, component, connecting supply, feeder, and control circuit.

Test continuity of each circuit.

* + - * 1. Tests and Inspections:

Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Perform the following infrared scan tests and inspections and prepare reports:

Initial Infrared Scanning: After Substantial Completion, but not more than sixty (60) days after Final Acceptance, perform an infrared scan of each switchboard. Remove front and side panels so joints and connections are accessible to portable scanner.

Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each switchboard eighteen (18) months after date of Substantial Completion.

Instruments and Equipment:

Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

Follow NFPA 70E requirements

Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

* + - * 1. Switchboard will be considered defective if it does not pass tests and inspections.
        2. Prepare test and inspection reports including a certified report that identifies switchboards included and that describes scanning results. Include notation of deficiencies detected, remedial action taken and observations after remedial action.
      1. ADJUSTING
         1. Adjust moving parts and operable components to function smoothly, and lubricate as recommended by manufacturer.
         2. Set field-adjustable circuit-breaker trip ranges as specified in Division 26 Section "Overcurrent Protective Device Coordination Study."
      2. PROTECTION
         1. Temporary Heating: Apply temporary heat, to maintain temperature according to manufacturer's written instructions, until switchboard is ready to be energized and placed into service.
      3. DEMONSTRATION
         1. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain switchboards, overcurrent protective devices, instrumentation, and accessories, and to use and reprogram microprocessor-based trip, monitoring, and communication units.

END OF SECTION 262413