SECTION 262816 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS

Latest Update 5-6-2017 See underlined text for Edits.

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”.)Last Update: 6.9.11. Reformatted and See Underlined Text.

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project.)

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this section and all other sections of Division 26.

      - SUMMARY

        - Section Includes:

          - Fusible switches.

          - Nonfusible switches.

          - Receptacle switches.

          - Shunt trip switches.

          - Molded-case circuit breakers (MCCBs).

          - Molded-case switches.

          - Enclosures.

      - DEFINITIONS

        - NC:  Normally closed.

        - NO:  Normally open.

        - SPDT:  Single pole, double throw.

      - SUBMITTALS

        - Product Data: For each type of enclosed switch, circuit breaker, accessory, and component indicated. Include dimensioned elevations, sections, weights, and manufacturers' technical data on features, performance, electrical characteristics, ratings, accessories, and finishes.

          - Enclosure types and details for types other than NEMA 250, Type 1.

          - Current and voltage ratings.

          - Short-circuit current ratings (interrupting and withstand, as appropriate).

          - Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices, accessories, and auxiliary components.

          - UMB Include time-current coordination curves (average melt) for each type and rating of overcurrent protective device; include selectable ranges for each type of overcurrent protective device

        - Shop Drawings: For enclosed switches and circuit breakers. Include plans, elevations, sections, details, and attachments to other work.

          - Wiring Diagrams: For power, signal, and control wiring.

        - Qualification Data: For qualified testing agency.

        - Field quality-control reports.

          - Test procedures used.

          - Test results that comply with requirements.

          - Results of failed tests and corrective action taken to achieve test results that comply with requirements.

        - Manufacturer's field service report.

        - Operation and Maintenance Data: For enclosed switches and circuit breakers to include in emergency, operation, and maintenance manuals. In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

          - Manufacturer's written instructions for testing and adjusting enclosed switches and circuit breakers.

      - Time-current coordination curves (average melt) for each type and rating of overcurrent protective device; include selectable ranges for each type of overcurrent protective device QUALITY ASSURANCE

        - Testing Agency Qualifications: Member company of NETA or an NRTL.

          - Testing Agency's Field Supervisor: Currently certified by NETA to supervise on-site testing.

        - Source Limitations: Obtain enclosed switches and circuit breakers, overcurrent protective devices, components, and accessories, within same product category, from single source from single manufacturer.

        - Product Selection for Restricted Space: Drawings indicate maximum dimensions for enclosed switches and circuit breakers, including clearances between enclosures, and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Comply with NFPA 70.

      - PROJECT CONDITIONS

        - Environmental Limitations: Rate equipment for continuous operation under the following conditions unless otherwise indicated:

          - Ambient Temperature: Not less than minus 220F and not exceeding 1040F.

          - Altitude:  Not exceeding six thousand six hundred (6,600) feet.

        - Interruption of Existing Electric Service: Do not interrupt electric service to facilities occupied by UMB or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

          - Notify UMB no fewer than ten (10) days in advance of proposed interruption of electric service.

          - Indicate method of providing temporary electric service.

          - Do not proceed with interruption of electric service without UMB’s written permission.

          - Comply with NFPA 70E.

      - COORDINATION

        - Coordinate layout and installation of switches, circuit breakers, and components with equipment served and adjacent surfaces. Maintain required workspace clearances and required clearances for equipment access doors and panels.

      - EXTRA MATERIALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Fuses:  Equal to 10 % of quantity installed for each size and type, but no fewer than three of each size and type.

          - Fuse Pullers:  Two (2) for each size and type.

      - WARRANTY/GUARANTEE

        - See Division 26 Specification Section “Basic Electrical Requirements’ for warranty and guarantee requirements.

- PRODUCTS

      - FUSIBLE SWITCHES

        - Manufacturers: Subject to compliance with requirements, provide products by one (1) of the following]:

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Square D; a brand of Schneider Electric.

        - Type GD, General Duty, Single Throw, 240 600 -V ac, 800 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with cartridge fuse interiors to accommodate [specified] [indicated] fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.  Fuses shall be rated for an interrupting capacity of 200,000 amps. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.  Fuses shall be rated for an interrupting capacity of 200,000 amps. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position. Fuses shall be rated for an interrupting capacity of 200,000 amps. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.  Fuses shall be rated for an interrupting capacity of 200,000 amps. <Engineer to Edit for Project Requirements>

        - Accessories:

          - Equipment Ground Kit: Internally mounted and labeled for copper ground conductors.

          - Neutral Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper neutral conductors.

          - Isolated Ground Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper neutral conductors.

          - Class R Fuse Kit:  Provides rejection of other fuse types when Class R fuses are specified.

          - Auxiliary Contact Kit: [One] [Two] NO/NC (Form "C") auxiliary contact(s), arranged to activate before switch blades open. <Engineer to Edit for Project Requirements>

          - Hookstick Handle:  Allows use of a hookstick to operate the handle.

          - Lugs:  Mechanical type, suitable for number, size, and conductor material.

          - Service-Rated Switches:  Labeled for use as service equipment.

          - Accessory Control Power Voltage:  Remote mounted and powered; [24-V ac] [120-V ac] [208-V ac] [12-V dc] [24-V dc]. <Engineer to Edit for Project Requirements>

      - NONFUSIBLE SWITCHES

        - Manufacturers:  Subject to compliance with requirements, provide products by one (1) of the following:

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Square D; a brand of Schneider Electric.

        - Type GD, General Duty, Single Throw, 240-V ac 600 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

        - Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position. <Engineer to Edit for Project Requirements>

        - Accessories:

          - Equipment Ground Kit: Internally mounted and labeled for copper ground conductors.

          - Neutral Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper neutral conductors.

          - Isolated Ground Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper neutral conductors.

          - Auxiliary Contact Kit: [One] [Two] NO/NC (Form "C") auxiliary contact(s), arranged to activate before switch blades open.<Engineer to Edit for Project Requirements>

          - Hookstick Handle:  Allows use of a hookstick to operate the handle.

          - Lugs:  Mechanical type, suitable for number, size, and conductor material.

          - Accessory Control Power Voltage:  Remote mounted and powered; [24-V ac] [120-V ac] [208-V ac] [12-V dc] [24-V dc]. <Engineer to Edit for Project Requirements>

      - RECEPTACLE SWITCHES

        - Manufacturers:  Subject to compliance with requirements, provide products by one (1) of the following:

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Square D; a brand of Schneider Electric.

        - Type HD, Heavy-Duty, Single-Throw Fusible Switch: [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.  Fuses shall be rated for an interrupting capacity of 200,000 amps. <Engineer to Edit for Project Requirements>

        - Type HD, Heavy-Duty, Single-Throw Nonfusible Switch:  [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, lockable handle with capability to accept three padlocks; interlocked with cover in closed position. <Engineer to Edit for Project Requirements>

        - Interlocking Linkage: Provided between the receptacle and switch mechanism to prevent inserting or removing plug while switch is in the on position, inserting any plug other than specified and turning switch on if an incorrect plug is inserted or correct plug has not been fully inserted into the receptacle.

        - Receptacle: Polarized, three-phase, four-wire receptacle (fourth wire connected to enclosure ground lug).

          - Receptacle Manufacturer and Catalog Number:  <Insert manufacturer and catalog number>.

      - SHUNT TRIP SWITCHES

        - Manufacturers: Subject to compliance with requirements, provide products by one (1) of the following:

          - Cooper Bussmann, Inc.

          - Ferraz Shawmut, Inc.

          - Littelfuse, Inc.

        - Show voltage and ampere ratings of shunt trip switches and fuses on Drawings.  General Requirements:  Comply with ASME A17.1, UL 50, and UL 98, with 200-kA interrupting and short-circuit current rating when fitted with Class J fuses.

        - Switches:  Three-pole, horsepower rated, with integral shunt trip mechanism and Class J fuse block; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

        - Control Circuit:  120-V ac; obtained from [integral control power transformer, with primary and secondary fuses,] <Insert source of control power> with a control power [transformer] [source] of enough capacity to operate shunt trip, connected pilot, and indicating and control devices. <Engineer to Edit for Project Requirements>

        - Accessories:

          - Oil tight key switch for key-to-test function.

          - Oil tight [red] [green] [white] [yellow] ON pilot light.<Engineer to Edit for Project Requirements>

          - Isolated neutral lug; [100] [200] percent rating.<Engineer to Edit for Project Requirements>

          - Mechanically interlocked auxiliary contacts that change state when switch is opened and closed.

          - Form C alarm contacts that change state when switch is tripped.

          - Three-pole, double-throw, fire-safety and alarm relay; [120-V ac] [24-V dc] coil voltage. <Engineer to Edit for Project Requirements>

          - Three-pole, double-throw, fire-alarm voltage monitoring relay complying with NFPA 72.

      - MOLDED-CASE CIRCUIT BREAKERS

        - Manufacturers: Subject to compliance with requirements, provide products by one (1) of the following:

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Square D; a brand of Schneider Electric.

        - General Requirements: Comply with UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents.

        - Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

        - Adjustable, Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

        - Electronic Trip Circuit Breakers: Field-replaceable rating plug, rms sensing, with the following field-adjustable settings:

          - Instantaneous trip.

          - Long- and short-time pickup levels.

          - Long- and short-time time adjustments.

          - Ground-fault pickup level, time delay, and I2t response.

        - Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller, and let-through ratings less than NEMA FU 1, RK-5.

        - Integrally Fused Circuit Breakers: Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker and trip activation on fuse opening or on opening of fuse compartment door.

        - Ground-Fault, Circuit-Interrupter (GFCI) Circuit Breakers: Single- and two-pole configurations with Class A ground-fault protection (6-mA trip).

        - Ground-Fault, Equipment-Protection (GFEP) Circuit Breakers:  With Class B ground-fault protection (30-mA trip).

        - Features and Accessories:

          - Standard frame sizes, trip ratings, and number of poles.

          - Lugs: Mechanical type, suitable for number, size, trip ratings, and conductor material.

          - Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge lighting circuits.

Retain first option in first subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units.

          - Ground-Fault Protection: Comply with UL 1053; [integrally mounted, self-powered] [remote-mounted and powered] type with mechanical ground-fault indicator; relay with adjustable pickup and time-delay settings, push-to-test feature, internal memory, and shunt trip unit; and three-phase, zero (0) sequence current transformer/sensor. <Engineer to Edit for Project Requirements>

          - Communication Capability: [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system, specified in Division 26 Section "Electrical Power Monitoring and Control." <Engineer to Edit for Project Requirements>

          - Shunt Trip:  Trip coil energized from separate circuit, with coil-clearing contact.

An optional time-delay unit, which allows an adjustable time delay in release of the trip coil for overriding momentary fluctuations, is available for the undervoltage trip unit in first subparagraph below.

          - Undervoltage Trip:  Set to operate at 35% to 75% of rated voltage without intentional time delay.

          - Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.<Engineer to Edit for Project Requirements>

          - Alarm Switch:  One [NO] [NC] contact that operates only when circuit breaker has tripped. <Engineer to Edit for Project Requirements>

          - Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

Retain first option in first subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units.

          - Zone-Selective Interlocking:  Integral with [electronic] [ground-fault] trip unit; for interlocking ground-fault protection function. <Engineer to Edit for Project Requirements>

          - Electrical Operator:  Provide remote control for on, off, and reset operations.

Retain subparagraph below if retaining options requiring integral or remote-control power in subparagraphs above and if control power for remote indication or operation is not specified in other Sections.

          - Accessory Control Power Voltage: [Integrally mounted, self-powered] [Remote mounted and powered]; [24-V ac] [120-V ac] [208-V ac] [12-V dc] [24-V dc]. <Engineer to Edit for Project Requirements>

      - MOLDED-CASE SWITCHES

        - Manufacturers: Subject to compliance with requirements, provide products by one (1) of the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Square D; a brand of Schneider Electric.

        - General Requirements:  MCCB with fixed, high-set instantaneous trip only, and short-circuit withstand rating equal to equivalent breaker frame size interrupting rating.

        - Features and Accessories:

          - Standard frame sizes and number of poles.

          - Lugs:  Mechanical type, suitable for number, size, trip ratings, and conductor material.

          - Ground-Fault Protection: Comply with UL 1053; remote-mounted and powered type with mechanical ground-fault indicator; relay with adjustable pickup and time-delay settings, push-to-test feature, internal memory, and shunt trip unit; and three-phase, zero-sequence current transformer/sensor.

          - Shunt Trip:  Trip coil energized from separate circuit, with coil-clearing contact.

An optional time-delay unit, which allows an adjustable time delay in release of the trip coil for overriding momentary fluctuations, is available for the undervoltage trip unit in first subparagraph below.

          - Under voltage Trip: Set to operate at 35% to 75% of rated voltage without intentional time delay.

          - Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic switch contacts, "b" contacts operate in reverse of switch contacts. <Engineer to Edit for Project Requirements>

          - Alarm Switch: One [NO] [NC] contact that operates only when switch has tripped. <Engineer to Edit for Project Requirements>

          - Key Interlock Kit:  Externally mounted to prohibit switch operation; key shall be removable only when switch is in off position.

          - Zone-Selective Interlocking: Integral with ground-fault shunt trip unit; for interlocking ground-fault protection function.

          - Electrical Operator:  Provide remote control for on, off, and reset operations.

Retain subparagraph below if retaining options requiring integral or remote-control power in subparagraphs above and if control power for remote indication or operation is not specified in other Sections.

          - Accessory Control Power Voltage: [Integrally mounted, self-powered] [Remote mounted and powered]; [24-V ac] [120-V ac] [208-V ac] [12-V dc] [24-V dc]. <Engineer to Edit for Project Requirements>

      - ENCLOSURES

        - Enclosed Switches and Circuit Breakers:  NEMA AB 1, NEMA KS 1, NEMA 250, and UL 50, to comply with environmental conditions at installed location.

          - Indoor, Dry and Clean Locations:  NEMA 250, [Type 1] <Insert type>.

          - Outdoor Locations:  NEMA 250, Type 4X non-metallic<Insert type>.

          - Other Wet or Damp, Indoor Locations:  NEMA 250, Type 4X non-metallic.

          - Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids:  NEMA 250, Type 12.

          - Hazardous Areas Indicated on Drawings: NEMA 250, [Type 7] [Type 9] <Insert type>.

- EXECUTION

      - EXAMINATION

        - Examine elements and surfaces to receive enclosed switches and circuit breakers for compliance with installation tolerances and other conditions affecting performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install individual wall-mounted switches and circuit breakers with tops at uniform height unless otherwise indicated.

        - Install individual floor-mounted switches and circuit breakers with tops at uniform height, utilizing properly secured channels anchored to floor and ceiling.

        - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

        - Install fuses in fusible devices.

        - Comply with NECA 1.

      - IDENTIFICATION

        - Comply with requirements in Division 26 Section "Identification for Electrical Systems."

          - Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

          - Label each enclosure with engraved metal or laminated-plastic nameplate.

      - FIELD QUALITY CONTROL

        - Testing Agency: UM Engage a qualified testing agency to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

        - Perform tests and inspections.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

        - Acceptance Testing Preparation:

          - Test insulation resistance for each enclosed switch and circuit breaker, component, connecting supply, feeder, and control circuit.

          - Test continuity of each circuit.

        - Tests and Inspections:

          - Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

          - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

          - Perform the following infrared scan tests and inspections and prepare reports:

            - Initial Infrared Scanning: After Substantial Completion, but not more than sixty (60) days after Final Acceptance, perform an infrared scan of each enclosed switch and circuit breaker. Remove front panels so joints and connections are accessible to portable scanner.

            - Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each enclosed switch and circuit breaker eleven (11) months after date of Substantial Completion.

            - Instruments and Equipment: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

          - Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

        - Enclosed switches and circuit breakers will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports including a certified report that identifies enclosed switches and circuit breakers and that describes scanning results.  Include notation of deficiencies detected, remedial action taken and observations after remedial action.

      - ADJUSTING

        - Adjust moving parts and operable components to function smoothly, and lubricate as recommended by manufacturer.

        - Set field-adjustable circuit-breaker trip ranges as specified in Division 26 Section "Overcurrent Protective Device Coordination Study".

END OF SECTION 262816